# Asset & Equipment Maintenance Log

Document No:  AEML-2026-V1.0

Revision:  1.0

Effective Date:  2026-01-27

# 1. Asset Identification

| Asset ID | SRV-DC01-001 |
| --- | --- |
| Asset Name / Type | Primary Domain Controller Server |
| Manufacturer | Dell |
| Model No. | PowerEdge R760 |
| Serial No. | ABC123XYZ456 |
| Location | Data Center, Rack 4, U-22 |
| Installation Date | 2025-03-15 |
| Warranty Expiry | 2028-03-14 |
| Assigned Department | IT Infrastructure |
| Criticality Level | High |

# 2. Preventive Maintenance Schedule

| Task ID | Asset Type | Task Description | Frequency | Next Due Date | Assigned To | Status |
| --- | --- | --- | --- | --- | --- | --- |
| PM-SRV-001 | Server | Review system logs for critical errors and warnings. | Daily | 2026-01-28 | NOC Team | Scheduled |
| PM-WKS-001 | Workstation | Run full antivirus scan and apply OS security patches. | Weekly | 2026-02-02 | IT Support | Scheduled |
| PM-SRV-002 | Server | Physically clean air intakes, fans, and check internal components. | Monthly | 2026-02-15 | NOC Team | Scheduled |
| PM-NET-001 | Network Equipment | Backup router and switch configurations. | Monthly | 2026-02-20 | Network Admin | Scheduled |
| PM-UPS-001 | UPS | Perform battery self-test and check load percentage. | Quarterly | 2026-03-10 | Facilities | Scheduled |
| PM-GEN-001 | Generator | Perform no-load test run for 15 minutes. | Quarterly | 2026-03-25 | Facilities | Scheduled |
| PM-SOL-001 | Solar Panels | Visual inspection for damage, debris, and soiling. Clean panels. | Quarterly | 2026-04-01 | Facilities | Scheduled |
| PM-SRV-003 | Server | Verify backup integrity by performing a test restore. | Quarterly | 2026-04-15 | SysAdmin | Scheduled |
| PM-GEN-002 | Generator | Perform full load test with Automatic Transfer Switch (ATS). | Annually | 2026-07-01 | Certified Vendor | Scheduled |
| PM-UPS-002 | UPS | Full battery rundown test and calibration. | Annually | 2026-09-01 | Certified Vendor | Scheduled |

# 3. Corrective Maintenance Log

| Log ID | Date Reported | Asset ID | Problem Description | Action Taken | Technician | Date Resolved | Status |
| --- | --- | --- | --- | --- | --- | --- | --- |
| CM-001 | 2026-01-15 | SRV-DC01-001 | Server overheating alerts. iDRAC reports Fan 3 failure. | Inspected server, confirmed Fan 3 not spinning. Ordered replacement fan (P/N: XYZ-789). Installed new fan, cleared alerts. Monitored temps for 2 hours, all nominal. | J. Doe | 2026-01-16 | Resolved |
| CM-002 | 2026-01-26 | UPS-MAIN-001 | UPS failed to transfer to battery during a brief power flicker. Building C lost power. | Initial investigation suggests a faulty transfer relay. Awaiting vendor diagnosis. Bypassed UPS for critical loads as a temporary measure. | A. Smith | - | Open |
| [Auto-gen ID] | [Date] | [Asset ID] | [Detailed description of the issue] | [Steps taken to resolve the issue] | [Name/ID] | [Date] | [Open/Resolved] |

# 4. Detailed Maintenance Task Checklists

## 4.1 Server Maintenance Checklist (Quarterly)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 1.1 | Physical Inspection: Check for loose cables, physical damage. | All connections secure, no visible damage. |  |  |  |
| 1.2 | Hardware Cleaning: Clean air vents, fans, and chassis interior of dust. | No significant dust buildup. Airflow is unobstructed. |  |  |  |
| 1.3 | Hardware Health Check: Review logs (iDRAC/iLO) for hardware errors. | No predictive failures or errors for PSU, RAM, CPU, Fans. |  |  |  |
| 1.4 | RAID Array Status: Check health of RAID controller and all physical disks. | Array status: Optimal. All disks: Online/OK. |  |  |  |
| 1.5 | Firmware/Driver Review: Check for critical firmware updates (BIOS, RAID, NIC). | Firmware is within N-1 version compliance. |  |  |  |
| 1.6 | Backup Verification: Perform a test restore of a random file/folder. | Restore successful, data integrity confirmed. |  |  |  |

## 4.2 Generator Maintenance Checklist (Quarterly)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 2.1 | Visual Inspection: Check for leaks (oil, fuel, coolant), damage, loose parts. | No visible leaks or damage. |  |  |  |
| 2.2 | Fluid Levels: Check engine oil, coolant, and fuel levels. | Oil: Full. Coolant: Full. Fuel: > 80%. |  |  |  |
| 2.3 | Battery Check: Check voltage and inspect terminals for corrosion. | Voltage > 12.4V (or 24.8V). Terminals clean. |  |  |  |
| 2.4 | No-Load Test Run: Start generator and run for 15 minutes. | Starts within 10s. Runs smoothly. |  |  |  |
| 2.5 | Check Block Heater: Verify block heater is operational. | Engine block is warm to the touch. |  |  |  |
| 2.6 | Automatic Transfer Switch (ATS): Check indicator lights and status. | ATS indicates "Normal Power". No alarms. |  |  |  |

## 4.3 UPS Maintenance Checklist (Quarterly)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 3.1 | Visual Inspection: Check for alarms, dust buildup, and fan operation. | No active alarms. Fans running quietly. |  |  |  |
| 3.2 | Check UPS Status: Record input/output voltage, load, and battery charge. | Input/Output within ±5% of nominal. Load < 75%. Batt > 98%. |  |  |  |
| 3.3 | Perform Battery Self-Test: Initiate self-test via front panel or software. | Test completes successfully with "Pass" result. |  |  |  |
| 3.4 | Review Event Log: Check for past alarms or events. | No critical events logged since last check. |  |  |  |

## 4.4 Solar Panel & Inverter Checklist (Quarterly)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 4.1 | Panel Visual Inspection: Check for cracks, discoloration, delamination, soiling. | Panels are physically intact and free of major soiling. |  |  |  |
| 4.2 | Mounting & Racking Check: Inspect for loose bolts, corrosion, or damage. | All mounting hardware is secure. |  |  |  |
| 4.3 | Inverter Check: Inspect for alarms, fan operation, and dust buildup. | No alarms. Fans operating. Vents are clean. |  |  |  |
| 4.4 | Record Inverter Readings: Log DC input voltage, AC output voltage, and current power production. | Readings are consistent with current weather conditions. |  |  |  |

## 4.5 Network Equipment Checklist (Monthly)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 5.1 | Backup Configuration: Perform a full backup of the running configuration. | Backup completes successfully and is stored securely. |  |  |  |
| 5.2 | Log Review: Check logs for critical errors, flapping ports, high CPU usage. | No critical errors found. CPU < 20%. |  |  |  |
| 5.3 | Physical Inspection: Check status LEDs, fan operation, and cable connections. | All status LEDs are green/normal. Fans are operational. |  |  |  |
| 5.4 | Firmware Check: Review vendor advisories for security vulnerabilities. | Current firmware is not listed in any new critical advisories. |  |  |  |

## 4.6 Workstation / Industrial PC Checklist (As Needed / Annually)

| Item | Checkpoint / Task | Specification / Standard | Result (P/F/NA) | Remarks / Readings | Initials |
| --- | --- | --- | --- | --- | --- |
| 6.1 | Physical Cleaning: Clean keyboard, mouse, screen, and case vents. | Device is free of dust and grime. |  |  |  |
| 6.2 | OS & Software Updates: Apply all critical/security OS and application patches. | System is fully patched. |  |  |  |
| 6.3 | Antivirus/Malware Scan: Run a full system scan. | Scan completed with no threats detected. |  |  |  |
| 6.4 | Disk Health & Cleanup: Run disk cleanup and check S.M.A.R.T. status. | S.M.A.R.T. status is "OK". Freed up disk space. |  |  |  |
| 6.5 | (Industrial PC) Enclosure & I/O Check: Inspect enclosure seals and test I/O ports. | Seals are intact. All required I/O ports are functional. |  |  |  |

| Reviewed By: Name: ____________________ Date: ____________________ | Approved By: Name: ____________________ Date: ____________________ |
| --- | --- |

This document contains confidential information proprietary to the company. Unauthorized distribution or reproduction is strictly prohibited.